**15-150**

**1. State Building Code to be Amended:**

 [x]  International Building Code [ ]  State Energy Code

 [ ]  ICC ANSI A117.1 Accessibility Code [ ]  International Mechanical Code

 [ ]  International Existing Building Code [ ]  International Fuel Gas Code

 [ ]  International Residential Code [ ]  NFPA 54 National Fuel Gas Code

 [x]  International Fire Code [ ]  NFPA 58 Liquefied Petroleum Gas Code

 [ ]  Uniform Plumbing Code [ ]  Wildland Urban Interface Code

 **Section(s): IFC903.2.6 Exception #2 and 907.2.6.4**

 **Title: Group I-4**

**2. Proponent Name (Specific local government, organization or individual): see below**

**3. Designated Contact Person:**

 **Name: Traci Harvey**

 **Title: Fire Protection Engineer**

 **Address: 2120 N. Wilbur, Spokane Valley, WA 99206**

 **Office Phone: (509) 892-4183**

 **Cell: (509) 496-4345**

 **E-Mail address: harveyt@spokanevalleyfire.com**

**4. Proposed Code Amendment**. Reproduce the section to be amended by underlining all added language, striking through all deleted language. Insert new sections in the appropriate place in the code in order to continue the established numbering system of the code. If more than one section is proposed for amendment or more than one page is needed for reproducing the affected section of the code additional pages may be attached. (Examples on the SBCC [website](https://fortress.wa.gov/ga/apps/sbcc/Page.aspx?nid=191))

 **Code(s)** International Fire Code **Section(s) IFC903.2.6 Exception #2 (Revised) and 907.2.6.4 (New)**

903.2.6 #2 An automatic sprinkler system is not required where Group I-4 day care facilities have an occupant load of 50 or less ~~are at the level of exit discharge and where every room where care is provided has not fewer than one exterior exit door~~.

907.2.6.4 Group I-4 occupancies A manual fire alarm system that initiates the occupant notification signal utilizing an emergency voice/alarm communication system meeting the requirements of Section 907.5.2.2 and installed in accordance with Section 907.6 shall be installed in Group I-4 occupancies. When automatic sprinkler systems or smoke detectors are installed, such systems or detectors shall be connected to the building fire alarm system.

 Exceptions:

 1. A manual fire alarm system is not required in Group I-4 occupancies with an occupant load of 50 or less.

 2. Emergency voice/alarm communication systems meeting the requirements of Section 907.5.2.2 and installed in accordance with Section 907.6 shall not be required in Group I-4 occupancies with occupant loads of 100 or less, provided that activation of the manual fire alarm system initiates an approved occupant notification signal in accordance with Section 907.5